## Measuring Points
S.No | Feeder | Remarks
1 | Incomer | Recording with Capacitor ON and OFF condition
2 |  | APFC Banks – 140 kVAr, Reactors – Nil

## Transformer Limits
S.No | Feeder Name | APFC ON/OFF | Transformer Capacity | Voltage Rating | Full load current (Transformer rating) | Impedance %(Z) | Vector Group | Short circuit current (Isc) | Transformer full load amps (IL Measured) | Isc/I L | TDD -total demand distortion (IEEE standard) | Ithd %
|  |  | kVA | KV | Amps | % |  | Amps | Amps
1 | Incomer | ON | 800 | 11/0.433 | 1066.73 | 4.9 | Dyn11 | 21769.98 | 707.65 | 30.76 | 8 | 24.41
2 |  | OFF | 800 | 11/0.433 | 1066.73 | 4.9 | Dyn11 | 21769.98 | 707.65 | 30.76 | 8 | 24.41

## Harmonic Analysis
S.No | Feeder | Type | Date | Time | Current RMS | Voltage RMS | KW | KVAR | KVA | PF | DPF | Current THD | Voltage THD
1 | Incomer | ON | 2026-01-24 | 10:39:27 | 707.65 | 398.22 | 463.73 | 76.57 | 485.89 | 0.95 | 0.99 | 24.41 | 6.52
2 | Incomer | OFF | 2026-01-24 | 10:39:27 | 707.65 | 398.22 | 463.73 | 76.57 | 485.89 | 0.95 | 0.99 | 24.41 | 6.52

## Individual Harmonics
S.No | Feeder | Type | I1 | I2 | I3 | I4 | I5 | I6 | I7 | I8 | I9 | I10 | I11 | I12 | I13
1 | Incomer | ON | 100 | 0.23 | 0.13 | 0.05 | 19.97 | 0.05 | 11.03 | 0.08 | 0.15 | 0.07 | 6.47 | 0.04 | 4.58
2 | Incomer | OFF | 100 | 0.23 | 0.13 | 0.05 | 19.97 | 0.05 | 11.03 | 0.08 | 0.15 | 0.07 | 6.47 | 0.04 | 4.58

## Graphs
Load Profile
THD
Loading
Harmonic Spectrum
Power Triangle